## LOAD REPORT
LOAD REPORT
S.No. | REF. | AREA (Sqft) | AREA (Sqft) | MEW ACTIVITY | LOAD |  |  | HEIGHT FT | SUPPLY CFM | TOTAL CFM | FA CFM | EA CFM | MOTOR POWER (KW) | Total Cap. TR | Sqft/TON | TOTAL CAPACITY | GPM | ACH
[5 empty] | ELECTRIC (W/Ft²)/WATTS | LIGHT (W/Ft²) watts | PEOPLE
1 | AHU-CIN1-01 | VIP LOBBY, VIP M&F WC | 1399 | COMMUNITY HALL | 2.5 | 0.93 | 30 | 11.2 | 1300 | 7080 | 880 | 680 | 7.5 | 4.2 | 333.0952 | 19.7 | 29.55 | 4.978
|  | VIP KITCHEN | 870 |  | 34.2 btu/sqft SENSIBLE | 0.65 | 14 | 7 | 2000 |  |  |  |  | 5 | 174 |  |  | 19.7044
11.42 btu/sqft LATENT
|  | STORAGE (S-2) | 406 | OFFICE | 2.5 | 0.84 | 2 | 5 | 280 |  |  |  |  | 0.6 | 676.6667 |  |  | 8.2759
|  | STORAGE (S-3) | 433 |  | 2.5 | 0.84 | 2 | 5 | 300 |  |  |  |  | 0.6 | 721.6667 |  |  | 8.3141
|  | STORAGE (S-4) | 402 |  | 2.5 | 0.84 | 2 | 5 | 280 |  |  |  |  | 0.6 | 670 |  |  | 8.3582
|  | STORAGE (S-5) | 312 |  | 2.5 | 0.84 | 2 | 5 | 220 |  |  |  |  | 0.5 | 624 |  |  | 8.4615
|  | CINEMA LOBBY | 2314 |  | 2.5 | 0.93 | 70 | 11.2 | 2700 |  |  |  |  | 8.2 | 282.1951 |  |  | 6.2508
2 | AHU-CIN1-02 | MAIN KITCHEN | 700 |  | 34.2 btu/sqft SENSIBLE | 0.65 | 13 | 7.5 | 1600 | 1720 | 0 |  | 2.2 | 4.2 | 166.6667 | 4.6 | 6.9 | 18.2857
11.42 btu/sqft LATENT
|  | STORAGE KITCHEN | 193 |  | 2.5 | 0.84 | 2 | 5 | 120 |  |  |  |  | 0.2 | 965 |  |  | 7.4611
3 | AHU-CIN1-03 | CINEMA FOYER | 4251 |  | 2.5 | 0.93 | 140 | 21.3 | 5500 | 5500 | 950 | 750 | 7.5 | 16 | 265.6875 | 16 | 24 | 3.6445
4 | AHU-CIN2-01 | SERVER ROOM | 265 |  | 8000 | 0.84 | 1 | 10 | 2600 | 2700 | 20 |  | 1.5 | 3.3 | 80.303 | 3.3 | 4.95 | 58.8679
5 | FCU-CIN1-01 | MALE TOILET | 700 |  |  | 0.84 | 12 | 10 | 630 | 630 |  | 750 (TOILET) | 0.15 | 1.5 | 466.6667 | 1.5 | 2.25 | 5.4
6 | FCU-CIN1-02 | FEMALE TOILET | 635 |  |  | 0.84 | 12 | 10 | 630 | 630 |  | 1125 (TOILET | 0.15 | 1.5 | 423.3333 | 1.5 | 2.25 | 5.9528
7 | FCU-CIN1-03 | CONTOL ROOM | 130 |  | 2500 | 0.84 | 4 | 10 | 600 | 600 | 40 |  | 0.15 | 1.1 | 118.1818 | 1.1 | 1.65 | 27.6923
8 | FCU-CIN1-04 | MANAGER | 139 |  | 2.5 | 0.84 | 4 | 10 | 200 | 500 | 70 |  | 0.15 | 0.4 | 347.5 | 0.9 | 1.35 | 8.6331
|  | OFFICE | 172 |  | 2.5 | 0.84 | 4 | 10 | 200 |  |  |  |  | 0.4 | 430 |  |  | 6.9767
|  | CCTV | 43 |  | 2.5 | 0.84 | 1 | 10 | 100 |  |  |  |  | 0.1 | 430 |  |  | 13.9535
9 | FCU-CIN1-05 | IT ROOM | 75 |  | 1900 WATTS | 0.84 | 1 | 10 | 450 |  | 20 |  | 0.15 | 0.7 | 107.1429 | 0.7 | 1.05 | 36
10 | FCU-CIN1-06 | MANAGER ROOM (NEAR KITCHEN) | 96 |  | 2.5 | 0.84 | 2 | 10 | 120 | 240 | 30 |  | 0.15 | 0.3 | 320 | 0.5 | 0.75 | 7.5
|  | STORAGE S-1 | 116 |  | 2.5 | 0.84 | 2 | 5 | 120 |  |  |  |  | 0.2 | 580 |  |  | 12.4138
11 | FCU-CIN1-07 | STORAGE AND CLEANER ROOM (ST-03) | 118 |  | 2.5 | 0.84 | 3 | 10 | 200 | 200 | 20 |  | 0.15 | 0.6 | 196.6667 | 0.6 | 0.9 | 10.1695
12 | FCU-CIN2-01 | PROJECTOR ROOM (S-1) | 215 |  | 4000 | 0.65 | 1 | 13 | 750 | 1200 | 70 |  | 0.4 | 1.4 | 153.5714 | 2.3 | 3.45 | 16.1002
|  | STRORAGE PROJECTOR ROOM | 86 |  | 250 | 0.84 | 1 | 13 | 100 |  |  |  |  | 0.2 | 430 |  |  | 5.3667
|  | EC PROJECTOR ROOM (S-1) | 430 |  | 0 | 0.84 | 8 | 13 | 350 |  |  |  |  | 0.7 | 614.2857 |  |  | 3.7567
13 | FCU-CIN2-02 | PROJECTOR ROOM (S-2) dolby | 301 |  | 25000 btu/hr | 0.84 | 1 | 12 | 1500 | 1500 | 30 |  | 0.4 | 2.6 | 115.7692 | 2.6 | 3.9 | 24.9169
14 | FCU-CIN2-03A&B | PROJECTOR ROOM (S-3 & S-4)) | 772 |  | 8000 | 0.84 | 2 | 10 | 1600 | 2000 | 150 |  | 0.25 | 3 | 257.3333 | 3.8 | 5.7 | 12.4352
15 |  | EC-L2-05 | 705 |  | 0 | 0.84 | 7 | 10 | 400 |  |  |  |  | 0.8 | 881.25 |  |  | 3.4043
16 | FCU-CIN2-04 | ELECTRIC ROOM | 240 |  | 2500 | 0.84 | 1 | 10 | 550 | 550 | 20 |  | 0.15 | 1 | 240 | 1 | 1.5 | 13.75
17 | FCU-CIN2-05 | EC-L2-11,L2.12 | 365 |  |  | 0.65 | 7 | 13 | 200 | 250 | 30 |  | 0.1 | 0.5 | 730 | 0.5 | 0.75 | 2.529
18 | FCU-CIN2-06 | STORAGE | 40 |  | 2.5 | 0.84 | 2 | 10 | 70 | 970 | 150 | 200 (TOILET) | 0.25 | 0.2 | 200 | 2 | 3 | 10.5
|  | EMERGENCY EXIT | 215 |  | 2.5 | 0.65 | 4 | 10 | 100 |  |  |  |  | 0.3 | 716.6667 |  |  | 2.7907
|  | STAF ROOM (M&F) | 605 |  | 2.5 | 0.84 | 18 | 10 | 800 |  |  |  |  | 1.5 | 403.3333 |  |  | 7.9339
TOTAL | [10 empty] | 2480 | 3805 |  |  |  | 62.6 | 93.9

## EXHAUST FAN SCHEDULE
EXHAUST FAN SCHEDULE
S.NO | TAG NO | QTY | SERVING | CFM | FAN MOTOR POWER KW/EACH | TOTAL FAN MOTOR POWER KW | ESP (IN.WG) | POWER | REMARKS
1 | KEF-CIN1-001 | 1 | MAIN KITCHEN | 6500 | 3 | 3 | 1.5 | 415/3/50 | ROOF MOUNTED
2 | KEF-CIN1-002 | 1 | VIP KITCHEN | 4300 | 2.2 | 2.2 | 1.5 | 415/3/50 | ROOF MOUNTED
3 | EF-CIN2-01 | 1 | PROJECTOR ROOM (SC-2) | 2650 | 1.5 | 1.5 | 1.5 | 415/3/50 | ROOF MOUNTED

## FINAL SCHEDULE
UNIT SCHEDULE
|  | S.No. | EQUIPMENT TAG NO. | AREA SERVED |  | MEW ACTIVITY | SUPPLY AIR FAN | [5 empty] | EXHAUST AIR FAN |  |  |  |  | HRU FLOW RATIO | COOLING COIL | [6 empty] | POWER | REMARKS
|  |  |  | FLOOR | SPACE |  | FA (l/s) | EA (CFM) | SA (l/s) | ESP (Pa) | FAN MOTOR POWER (KW) | SPEED CONTROL | EA/Unit (l/s) | RA/Unit (l/s) | ESP (Pa) | FAN MOTOR POWER (KW) | SPEED CONTROL |  | ON COIL |  | OFF COIL |  | TC (KW) | SC (KW) | CHW (L/S)
[19 empty] | DB (ºC) | WB (ºC) | DB (ºC) | WB (ºC)
|  | 1 | AHU-R-CIN2-001 | LEVEL-1 | SCREEN-1 | COMMUNITY HALL | 826 | 680 | 2027 | 300 | 4 | VARIBLE | 751 | 1201 | 250 | 0.75 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 61.8 | 39.08 | 1.624 | 415/3/50
|  | 2 | AHU-R-CIN2-002 | LEVEL-1 | SCREEN-2 | COMMUNITY HALL | 980 | 680 | 2406 | 300 | 4 | VARIBLE | 892 | 1426 | 250 | 1.1 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 72.56 | 46.37 | 1.926 | 415/3/50
|  | 3 | AHU-R-CIN2-003 | LEVEL-1 | SCREEN-3 | COMMUNITY HALL | 928 | 680 | 2277 | 300 | 4 | VARIBLE | 844 | 1349 | 250 | 1.1 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 68.72 | 43.9 | 1.824 | 415/3/50
|  | 4 | AHU-R-CIN2-004 | LEVEL-1 | SCREEN-4 | COMMUNITY HALL | 1023 | 680 | 2513 | 300 | 5.5 | VARIBLE | 932 | 1490 | 250 | 1.1 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 75.73 | 48.41 | 2.01 | 415/3/50
|  | 5 | AHU-R-CIN2-005 | LEVEL-1 | SCREEN-5 | COMMUNITY HALL | 866 | 680 | 2126 | 300 | 4 | VARIBLE | 788 | 1260 | 250 | 0.75 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 64.13 | 40.97 | 1.702 | 415/3/50
|  | 6 | AHU-R-CIN2-006 | LEVEL-1 | SCREEN-6 | COMMUNITY HALL | 866 | 680 | 2126 | 300 | 4 | VARIBLE | 788 | 1260 | 250 | 0.75 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 64.13 | 40.97 | 1.702 | 415/3/50
|  | 7 | AHU-R-CIN2-007 | LEVEL-1 | VIP SCREEN-1 | COMMUNITY HALL | 297 | 680 | 729 | 300 | 1.5 | VARIBLE | 270 | 432 | 250 | 0.25 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 22 | 14.05 | 0.584 | 415/3/50
|  | 8 | AHU-R-CIN2-008 | LEVEL-1 | VIP SCREEN-2 | COMMUNITY HALL | 402 | 680 | 987 | 300 | 1.5 | VARIBLE | 366 | 585 | 250 | 0.37 | VARIBLE | 91% | 29.4 | 21.1 | 13.5 | 12.9 | 29.76 | 19.2 | 0.79 | 415/3/50
NOTE:
1 | ALL AHU SHALL BE DOUBLE SKIN OF 40MM THICKNESS PANEL
2 | CONTRACTOR TO SUBMIT NOISE LEVEL DATABASE ON FINAL SELECTION OF EQUIPMENT & TO COMPLY WITH NOISE CRITERIA MENTIONED IN SPECEFICATION
3 | ALL AHU SHALL BE ADJUSTABLE PULLEY
4 | UNITS WITH MORE THAN ONE HORSE POWER TO BE SUPPLIED WITH 3-phase MOTOR
5 | THE CONTRACTOR SHALL VERIFY INTERNAL & EXTERNAL STATIC PRESSURE FOR EACH AS PER ACTUAL EQUIPMENT & SHOP DRAWINGS & ACCORDINGLY MOTORS SHALL BE SELECTED WITHOUT ANY EXTRA COST OR TIME
6 | THE CONTRACTOR SHALL CONSIDER FILTER PRESSURE DROP (ASSUME 50% DIRT) WHILE CALCULATING TOTAL PRESSURE FOR FAN
7 | VELOCITY OVER COIL SHALL NOT EXCEED 2.00 m/s
8 | EACH UNIT SHALL BE PROVIDED WITH SPRING ISOLATOR TYPE (H) & SHALL BE MOUNTED AS RECOMMENDED BY MANUFACTURER
9 | HIGH EFFICIENCY MOTOR AND FAN SHALL BE MANDATORY
10 | MOTOR TO BE SUPPLIED COMPLET WITH DB,DRIVES,INSTRUMENTATION AND CONTROL AS REQUIRED
11 | MINIMUM FAN EFFICIENCY SHALL BE 80%
12 | MINIMUM MOTOR FAN EFFICIENCY SHALL BE 90% (CLASS-1)
13 | SOUND POWER OF ALL AHU FANS SHALL NOT BE MORE THAN 80 db
14 | SELECT COOLING COIL WITH 10% EXTRA CAPACITY (CONSIDERING SAME AIR FLOW RATE AND ON COIL TEMPRATURE
15 | All AHU shall be provided with a factory assembled spring isolator under the blower and the electric motor.The selection of spring should be according to the manufacturers instruction and on design efficiency criteria in all cases, it shall be not be less than one inch deflection
16 | ALL AHU SERVING CINEMA SHOULD BE VFD MOTOR
17 | HIGH EFFICIENCY MOTOR AND FAN SHALL BE MANADTORY
18 | MOTOR TO BE SUPPLIED COMPLET WITH DB,DRIVES,INSTRUMENTATION AND CONTROL AS REQUIRED
19 | PROVIDE SOUND ATTENUATOR WHEREVER REQUIRED TO MAINTAIN NOISE EQUAL OR LOWER THAN REQUIRED VALUE WITHOUT ANY EXTRA COST AND TIME
20 | FCU FAN SHALL BE 3-SPEED.FAN SHALL BE SELECTED AT MEDIUM SPEED